## UPC Formula
Unified Plumbing Code Method Grease Interceptor Sizing Worksheet
Links to CSI Grease Interceptor Drawings
IAPMO DESIGNS (4' DIAMETER)
4' - 900 Gallon
Business Name: | [7 empty] | Date: | [5 empty] | 4' - 1,300 Gallon
4' - 1,800 Gallon
Address: | [7 empty] | Calculated By:
IAPMO DESIGNS (6' DIAMETER)
6' - 1,900 Gallon
Follow these six simple steps to determine grease interceptor size (enter calculations below): | [13 empty] | 6' - 2,300 Gallon
6' - 2,800 Gallon
No. of Meals | [9 empty] | Calculated |  |  |  | 6' - 3,400 Gallon
Per Peak |  | Waste Flow |  |  | Retention |  | Storage |  |  | Liquid |  | Grease |  | 6' - 4,400 Gallon
Hour |  | Rate |  |  | Time |  | Factor |  |  | Capacity |  | Interceptor |  | 6' - 5,200 Gallon
0 |  | 0 |  |  | 0 |  | 0 |  |  | 0
| X |  |  | X |  | X |  |  | =
IAPMO DESIGNS (8' DIAMETER)
Step 1 |  | Step 2 |  |  | Step 3 |  | Step 4 |  |  | Step 5 |  | Step 6 |  | 8' - 3,300 Gallon
8' - 4,100 Gallon
1 | Number of Meals Per Peak Hour (Recommended Formula): | [9 empty] | Notes:
|  | Seating |  |  |  |  | Meals Per | [6 empty] | 8' - 4,900 Gallon
|  | Capacity |  |  | Meal Factor |  | Peak Hour | [6 empty] | 8' - 5,700 Gallon
|  |  |  | X |  | = | 0 | [6 empty] | 8' - 6,400 Gallon
8' - 7,900 Gallon
| Establishment Type: | [5 empty] | Meal Factor: | [6 empty] | 8' - 9,500 Gallon
|  | Fast Food (45 min.) |  |  |  |  | 1.33 | [6 empty] | 8' - 12,000 Gallon
|  | Resteraunt (60 min.) |  |  |  |  | 1
|  | Leisure Dining (90 min.) |  |  |  |  | 0.67 | [6 empty] | IAPMO DESIGNS (10' DIAMETER)
|  | Dinner Club (120 min.) |  |  |  |  | 0.5 | [6 empty] | 10' - 7,400 Gallon
2 | Waste Flow Rate: | [9 empty] | Notes: |  |  | 10' - 8,600 Gallon
|  | Condition |  |  |  |  | Flow Rate:
|  | With a Dishwashing Machine |  |  |  |  | 6 gallons | [6 empty] | 10' - 11,000 Gallon
|  | Without a Dishwashing Machine |  |  |  |  | 5 gallons | [6 empty] | 10' - 15,000 Gallon
|  | Single Service Kitchen |  |  |  |  | 2 gallons | [6 empty] | 10' - 18,000 Gallon
|  | Food Waste Disposal Only |  |  |  |  | 1 gallons | [6 empty] | 10' - 22,000 Gallon
3 | Retention Time: | [9 empty] | Notes:
|  | Commercial Kitchen |  |  |  |  | 2.5 hours | [6 empty] | 10' - 25,000 Gallon
|  | Single Service Kitchen |  |  |  |  | 1.5 hours | [6 empty] | 10' - 29,000 Gallon
4 | Storage Factor: | [9 empty] | Notes: |  |  | IAPMO DESIGNS (12' DIAMETER)
12' - 17,000 Gallon
|  | Kitchen Type |  |  |  |  | Storage | [6 empty] | 12' - 20,000 Gallon
|  | 1. Fully Equipped Commercial |  |  |  |  | Factor: | [6 empty] | 12' - 24,000 Gallon
|  |  | Hours of Operation | [10 empty] | 12' - 27,000 Gallon
|  |  | 8 hours |  |  |  | 1 | [6 empty] | 12' - 31,000 Gallon
|  |  | 12 hours |  |  |  | 1.5 | [6 empty] | 12' - 33,000 Gallon
|  |  | 16 hours |  |  |  | 2 | [6 empty] | 12' - 34,000 Gallon
|  |  | 24 hours |  |  |  | 3
|  | 2. Single Service |  |  |  |  | 0.5
5 | Calculated Liquid Capacity: | [9 empty] | Notes:
Multiply the values obtained from steps 1, 2, 3 and 4. The result
is the approximate grease interceptor size for this business.
6 | Select Grease Interceptor: | [9 empty] | Notes:
Using the approximate required liquid capacity from step 5, select
appropriate size grease interceptor.
THIS WORKSHEET IS INTENDED FOR ESTIMATING THE SIZE OF A GREASE INTERCEPTOR ONLY!
THE FINAL DETERMINATION FOR THE SIZE OF THE GREASE INTERCEPTOR WILL BE MADE BY THE
APPROPRIATE RWU PERSONNEL.
©2011 Containment Solutions, Inc. • All Rights Reserved. • Pub. No. TNK 1095